## lOOP IMP
Earth Fault Loop Impedance Test
Location | Dest Point | Type | Current(A) | Multiplying factor | Imp (Z) | Z_Allowed | Z- Measured output | Results | Remarks(NOISE)
1. Power House&VCB room
i .POWER HOUSE socket | EQDB-01B-L1-B | C | 16 | 10 | 1.438 | 0.959 | 0.76 | PASS | NO
ii. VCB ROOM socket | SWITCH 20 | C | 32 | 10 | 0.719 | 0.479 | 0.8 | FAIL | NO
iii. STREET LIGHT | SWITCH 25(VCB ROOM) | C | 20 | 10 | 1.15 | 0.767 | 0.59 | PASS | NO
2 . BASEMENT-2
i.B2 NEAR STAIRCASE, SOUTH | LDB-02-B2 | C | 6 | 10 | 3.833 | 2.555 | 0.43 | PASS | NO
ii.B2 AT WAY OUT NEAR CAMERA, NORTH | LDB-01-B2 | C | 6 | 10 | 3.833 | 2.555 | 0.47 | PASS | NO
3. BASEMENT-1
i. B1 NEAR ELECTRICAL ROOM,NORTH | LDB-01-B1 | C | 6 | 10 | 3.833 | 2.555 | 0.65 | PASS | YES
ii. B1 NEAR ELECTRICAL ROOM,SOUTH | LDB-02-B1 | C | 6 | 10 | 3.833 | 2.555 | 0.5 | PASS | YES
iii.B1 AT DRINKING WAITER | EQDB-01-B1-R3 (SOCKET) | C | 16 | 10 | 1.438 | 0.959 | 1.25 | FAIL | NO
4. GROUND FLOOR
i. NEAR STAIRCASE | EQDB-02B-GF | C | 16 | 10 | 1.438 | 0.959 | 0.03 | PASS | NO
ii. NEAR RECEPTION 00 | LDB-02A-GF | C | 6 | 10 | 3.833 | 2.555 | 0.51 | PASS | NO
iii. NEAR RADIOLOGY 00 | LDB-01A-GF | C | 6 | 10 | 3.833 | 2.555 | 0.4 | PASS | NO
iv. NEAR ICT ROOM B026 | EQDB-01A-GF | C | 16 | 10 | 1.438 | 0.959 | 0.14 | PASS | NO
5. 1st FLOOR
i.OT-COMPLEX | LDB-01A-L1 | C | 6 | 10 | 3.833 | 2.555 | 0.41 | PASS | NO
ii. URGENT CARE,NEAR WAITING AREA 01 | LDB-02A-L1 | C | 6 | 10 | 3.833 | 2.555 | 0.48 | PASS | NO
iii. URGENT CARE,NEAR STAIRCASE | EQDB-02C-L1 | C | 16 | 10 | 1.438 | 0.959 | 0.09 | PASS | NO
6. 2nd FLOOR
i.CARDIOLOGY | EQDB-02D-L2 | C | 16 | 10 | 1.438 | 0.959 | 0.11 | PASS | NO
ii.NEAR WAITINGAREA02 | LDB-02A-L2 | C | 6 | 10 | 3.833 | 2.555 | 0.56 | PASS | YES
iii. INSIDE WAITINGAREA02 | LDB-01A-L2 | C | 6 | 10 | 3.833 | 2.555 | 0.68 | PASS | NO
iv. NEAR EMEGERNCY EXIT | EQDB-01A-L2 | C | 16 | 10 | 1.438 | 0.959 | 0.14 | PASS | NO
7. 3RD FLOOR
i. NEAR WAITING AREA 03 | LDB-02A-L3 | C | 6 | 10 | 3.833 | 2.555 | 0.47 | PASS | NO
ii. NEAR GERIATRICS | LDB-01A-L3 | C | 6 | 10 | 3.833 | 2.555 | 0.56 | PASS | NO
8. 4TH FLOOR
i.NEAR MASTER CHECKUP | LDB-01A-L4 | C | 6 | 10 | 3.833 | 2.555 | 0.8 | PASS | YES
ii. NEAR EMR/MRD 4A4 | LDB-02A-L4 | C | 6 | 10 | 3.833 | 2.555 | 0.46 | PASS | NO
iii.NEAR PAEDIATRICS | EQDB-02A-L4 | C | 16 | 10 | 1.438 | 0.959 | 0.14 | PASS | NO
iv.OPPOSITE TO STAFF STATION | FED from EQDB-02D-L4-R1 (SOCKET) | C | 16 | 10 | 1.438 | 0.959 | 0.34 | PASS | NO
v.INSIDE PAEDIATRICS,DRINKING WATER | FED from EQDB-02D-L4-Y5 (SOCKET) | C | 16 | 10 | 1.438 | 0.959 | 1.02 | FAIL | YES
vi. INSIDE KAAPPI 2.0 | FED from EQDB-01B-L4-B5(SOCKET) | C | 16 | 10 | 1.438 | 0.959 | 1.63 | FAIL | NO
9. 5TH FLOOR
i. ANANDHASS,DRINKING WATER | FED from EQDB-01D-Y2 | C | 16 | 10 | 1.438 | 0.959 | 0.53 | PASS | NO
ii. NEAR ADMINISTRATION 05 | LDB-02A-L5 | C | 6 | 10 | 3.833 | 2.555 | 0.4 | PASS | NO
iii.NEAR VIP DININGAREA B508 | LDB-01A-L5 | C | 6 | 10 | 3.833 | 2.555 | 0.6 | PASS | YES
iv. OPPOSITE HOUSE KEEPING B510 | EQDB-01B-L5 | C | 16 | 10 | 1.438 | 0.959 | 0.17 | PASS | NO
10. TERRACE
i. INSIDE STAFF DINING | SOCKET NEAR TABLE | C | 16 | 10 | 1.438 | 0.959 | 1.17 | FAIL | NO
ii. INSIDE STAFF DINING | SOCKET NEAR DRINKING WATER | C | 16 | 10 | 1.438 | 0.959 | 2.97 | FAIL | YES
iii. BACKYARD LIGHT | LED Drive panel,RIGHT SIDE | C | 40 | 10 | 0.575 | 0.383 | 1.87 | FAIL | YES
iv.BACKYARD LIGHT | LED Drive panel,LEFT SIDE | C | 40 | 10 | 0.575 | 0.383 | 1.69 | FAIL | YES

## RCBO
RCD TEST FOR THREE PHASE
sl.no | LOACTION |  | RCBO RATING |  | R-PHASE |  | Y-PHASE |  | B-PHASE
|  | DB | OVERLOAD CURVE | RESIDUAL CURRENT(ma) | TIME(ms) | STATUS | TIME(ms) | STATUS | TIME(ms) | STATUS
1 | BASEMENT-2
2 | B2 NEAR STAIRCASE, SOUTH | LDB-02-B2 | C25 | 30 | 17.5 | TRIP | 24.7 | TRIP | 17.9 | TRIP
3 | B2 AT WAY OUT NEAR CAMERA, NORTH | LDB-01-B2 | C25 | 30 | 21.3 | TRIP | 21.9 | TRIP | 31.3 | TRIP
4 | BASEMENT-1
5 | B1 NEAR ELECTRICAL ROOM,NORTH | LDB-01-B1 | C25 | 30 | 30.2 | TRIP | 17.9 | TRIP | 124 | TRIP
6 | B1 NEAR ELECTRICAL ROOM,SOUTH | LDB-02-B1 | C25 | 30 | 30.6 | TRIP | 30.9 | TRIP | 43.1 | TRIP
7 | GROUND
8 | NEAR STAIRCASE | EQDB-02B-GF | C40 | 100 | 45.3 | TRIP | 20.6 | TRIP | 22.5 | TRIP
9 | NEAR RECEPTION 00 | LDB-02A-GF | C25 | 30 | 32.5 | TRIP | 94.9 | TRIP | 30.9 | TRIP
10 | NEAR RADIOLOGY 00 | LDB-01A-GF | C25 | 30 | 28 | TRIP | 75.2 | TRIP | 17.6 | TRIP
11 | NEAR ICT ROOM B026 | EQDB-01A-GF | C40 | 100 | 20.4 | TRIP | 42.9 | TRIP | 10.4 | TRIP
12 | 1ST FLOOR
13 | OT-COMPLEX | LDB-01A-L1 | C25 | 30 | 11.5 | TRIP | 118 | TRIP | 31.4 | TRIP
14 | URGENT CARE,NEAR WAITING AREA-01 | LDB-02A-L1 | C25 | 30 | 71.7 | TRIP | 127.6 | TRIP | 78.2 | TRIP
15 | URGENT CARE,NEAR STAIRCASE | EQDB-02C-L1 | C40 | 100 | 30.2 | TRIP | 26.8 | TRIP | 46.9 | TRIP
16 | 2ND FLOOR
17 | CARDIOLOGY | EQDB-02D-L2 | C40 | 100 | 9.9 | TRIP | 45.6 | TRIP | 30.5 | TRIP
18 | NEAR WAITINGAREA-02 | LDB-02A-L2 | C25 | 30 | 33.8 | TRIP | 32 | TRIP | 31 | TRIP
19 | INSIDE WAITINGAREA-02 | LDB-01A-L2 | C25 | 30 | >550 | NO TRIP | >550 | NO TRIP | 69.3 | TRIP
20 | NEAR EMEGERNCY EXIT | EQDB-01A-L2 | C40 | 100 | >550 | NO TRIP | 17.8 | TRIP | 17.8 | TRIP
21 | 3RD FLOOR
22 | NEAR WAITING AREA-03 | LDB-02A-L3 | C25 | 30 | 25.7 | TRIP | 32.9 | TRIP | 31.2 | TRIP
23 | NEAR GERIATRICS | LDB-01A-L3 | C25 | 30 | 31 | TRIP | 31.6 | TRIP | 30.9 | TRIP
24 | 4TH FLOOR
25 | NEAR MASTER CHECKUP | LDB-01A-L4 | C25 | 30 | 31.1 | TRIP | 31.4 | TRIP | 31.1 | TRIP
26 | NEAR EMR/MRD 4-A4 | LDB-02A-L4 | C25 | 30 | 56.8 | TRIP | 11.4 | TRIP | 31 | TRIP
27 | NEAR PAEDIATRICS | EQDB-02A-L4 | C40 | 100 | 10.2 | TRIP | 12.8 | TRIP | 30.4 | TRIP
28 | 5TH FLOOR
29 | NEAR ADMINISTRATION-05 | LDB-02A-L5 | C25 | 30 | >550 | NO TRIP | 82.7 | TRIP | 31.2 | TRIP
30 | NEAR VIP DININGAREA-B508 | LDB-01A-L5 | C25 | 30 | 51.2 | TRIP | 30.8 | TRIP | 30.4 | TRIP
31 | OPPOSITE HOUSE KEEPING-B510 | EQDB-01B-L5 | C40 | 100 | 10.3 | TRIP | 41.4 | TRIP | 30.1 | TRIP